## Test Sheet
Customer | [18 empty] | Job # | [7 empty] | PASS
Address | [18 empty] | Technicians
User
Date |  |  |  |  | Temp. |  | 68 |  | °F | 20 |  | °C |  | TCF |  | 1.002 |  |  | Substation
Identifier | [12 empty] | Humidity |  |  |  | % |  | Eqpt. Location
Nameplate Data
|  |  |  | Phase |  |  |  | Neutral | [11 empty] | Phase |  |  |  | Neutral
|  | Manufacturer | [12 empty] | Voltage Rating (V)
|  | Catalog Number | [12 empty] | Frequency
|  | Type | [12 empty] | Burden
|  | Accuracy Class | [12 empty] | Polarity Facing
Visual and Mechanical Inspection
| NETA Section | [23 empty] | Results
| 7.10.1.A.1 |  | Compare equipment nameplate data with drawings and specifications. | [21 empty] | Select One
| 7.10.1.A.2 |  | Inspect physical and mechanical condition. | [21 empty] | Select One
| 7.10.1.A.3 |  | Verify correct connection of transformers with system requirements. | [21 empty] | Select One
| 7.10.1.A.4 |  | Verify that adequate clearances exist between primary and secondary circuit wiring. | [21 empty] | Select One
| 7.10.1.A.5 |  | Verify the unit is clean. | [21 empty] | Select One
| 7.10.1.A.6 |  | Use of a low-resistance ohmmeter in accordance with Section 7.10.1.B.1. | [21 empty] | Select One
| 7.10.1.A.7 |  | Verify that all required grounding and shorting connections provide contact. | [21 empty] | Select One
| 7.10.1.A.8 |  | Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces. | [21 empty] | Select One
CT Identification
|  | Phase A |  |  |  | Phase B | [8 empty] | Phase C | [7 empty] | Neutral
|  | Serial # |  |  |  | Serial # | [8 empty] | Serial # | [7 empty] | Serial #
|  | Ratio |  | : |  | Ratio |  |  |  |  | : |  |  |  | Ratio |  |  |  | : |  |  |  | Ratio |  |  | :
Electrical - Ratio & Burden Tests
Ratio and Burden Test
|  | Identifier |  | Calculated Ratio |  |  | Measured Ratio |  |  |  |  | Ratio dev. |  |  | Polarity |  | Measured Burden (Ω) | [5 empty] | Results
Electrical - Insulation Resistance Tests
|  | Primary Winding to Ground |  |  |  |  | Test Voltage (V): |  |  |  |  | 1000 |  | V |  | Table 100.5 Criteria |  |  |  |  | Results
|  | Identifier |  | Measured Values |  |  | Temp. Corrected |  |  |  |  | Units |  |  |  | Value |  | Units
[12 empty] | MΩ |  |  |  | ≥ |  | MΩ |  |  | N/A
[12 empty] | MΩ |  |  |  | ≥ |  | MΩ |  |  | N/A
[12 empty] | MΩ |  |  |  | ≥ |  | MΩ |  |  | N/A
[12 empty] | MΩ |  |  |  | ≥ |  | MΩ |  |  | N/A
|  | Secondary Winding to Ground |  |  |  |  | Test Voltage (V): |  |  |  |  | 1000 |  | V |  | Table 100.5 Criteria |  |  |  |  | Results
|  | Identifier |  | Measured Values |  |  | Temp. Corrected |  |  |  |  | Units |  |  |  | Value |  | Units
[12 empty] | MΩ |  |  |  | ≥ |  | MΩ |  |  | N/A
[12 empty] | MΩ |  |  |  | ≥ |  | MΩ |  |  | N/A
[12 empty] | MΩ |  |  |  | ≥ |  | MΩ |  |  | N/A
[12 empty] | MΩ |  |  |  | ≥ |  | MΩ |  |  | N/A
Test Equipment Used
| Megohmmeter: | [9 empty] | Serial Number: | [10 empty] | AMP ID:
| CT Ratio Test Set: | [9 empty] | Serial Number: | [10 empty] | AMP ID:
Comments: