## Test Sheet
Customer | [21 empty] | Job # | [5 empty] | PASS
Address | [21 empty] | Technicians
User
Date | [7 empty] | Temp. |  | 68 | °F | 20 |  | °C |  | TCF |  | 1.002 |  |  |  | Substation
Identifier | [14 empty] | Humidity |  |  |  | 72 | % |  | Eqpt. Location
Nameplate Data
|  |  |  | Manufacturer | [14 empty] | Voltage Rating
|  |  |  | Catalog Number | [14 empty] | Insulation Level (BIL)
|  |  |  | Serial Number | [14 empty] | Frequency
|  |  |  | Accuracy Class | [14 empty] | Buden
Visual and Mechanical Inspection
| NETA Section | [24 empty] | Results
| 7.10.2.A.1 |  | Compare equipment nameplate data with drawings and specifications. | [22 empty] | Satisfactory
| 7.10.2.A.2 |  | Inspect physical and mechanical condition. | [22 empty] | Satisfactory
| 7.10.2.A.3 |  | Verify correct connection of transformers with system requirements. | [22 empty] | Satisfactory
| 7.10.2.A.4 |  | Verify that adequate clearances exist between primary and secondary circuit wiring. | [22 empty] | Satisfactory
| 7.10.2.A.5 |  | Verify the unit is clean. | [22 empty] | Satisfactory
| 7.10.2.A.6.1 |  | Use of low-resistance ohmmeter in accordance with Section 7.10.2.B.1. | [22 empty] | Satisfactory
| 7.10.2.A.7 |  | Verify that all required grounding and connections provide contact. | [22 empty] | Satisfactory
| 7.10.2.A.8 |  | Verify correct primary and secondary fuse sizes for voltage transformers. | [22 empty] | Satisfactory
| 7.10.2.A.9 |  | Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces. | [22 empty] | Not Applicable
Fuse Data
[6 empty] | Manufacturer | [10 empty] | Voltage Rating (kV)
[6 empty] | Catalog Number | [10 empty] | Ampacity (A)
[6 empty] | Class | [10 empty] | I.C. Rating (kA)
Electrical - Fuse Resistance Test
|  | Fuse Resistance |  |  |  | As Found |  |  | As Left |  | Units
Electrical - Ratio & Burden Test
Ratio and Burden Test
|  | Pri. Voltage |  |  | Sec. Voltage |  |  |  |  | Calculated Ratio |  |  |  | Measured Ratio |  |  |  |  | % Dev. |  |  | Polarity |  | Measured Burden (Ω) |  |  | Results
|  | 240 |  |  | 120 |  |  |  |  | 2 |  |  |  | 1.996 |  |  |  |  | 0.2 |  |  | Yes |  |  |  |  | Pass
Electrical - Insulation Resistance Test
|  | Insulation Resitance 1 min. | [8 empty] | Test Voltage (V) |  |  |  |  | 1000 |  | V |  | Table 100.5 Criteria |  |  |  |  | Results
|  | Winding Under Test |  |  |  |  | Measured Values |  |  |  | Temp. Corrected |  |  |  |  | Units |  |  |  | Value |  |  | Units
|  | Primary to Ground |  |  |  |  | > |  | 2200 |  | > |  | 2204.4 |  |  | MΩ |  |  |  | ≥ | 500 |  | MΩ |  | PASS
|  | Secondary to Ground |  |  |  |  | > |  | 2200 |  | > |  | 2204.4 |  |  | MΩ |  |  |  | ≥ | 500 |  | MΩ |  | PASS
|  | Primary to Secondary |  |  |  |  | > |  | 2200 |  | > |  | 2204.4 |  |  | MΩ |  |  |  | ≥ | 500 |  | MΩ |  | PASS
Test Equipment Used
| Megohmmeter: | [11 empty] | Serial Number: | [10 empty] | AMP ID:
| Low-Resistance Ohmmeter: | [11 empty] | Serial Number: | [10 empty] | AMP ID:
| TTR Test Set: | [11 empty] | Serial Number: | [10 empty] | AMP ID:
Comments:

## TCF
Insulation Correction Factors (20C)
Tempurature | Multiplier
-24 | 0.054
-23 | 0.068
-22 | 0.082
-21 | 0.096
-20 | 0.11
-19 | 0.124
-18 | 0.138
-17 | 0.152
-16 | 0.166
-15 | 0.18
-14 | 0.194
-13 | 0.208
-12 | 0.222
-11 | 0.236
-10 | 0.25
-9 | 0.264
-8 | 0.278
-7 | 0.292
-6 | 0.306
-5 | 0.32
-4 | 0.336
-3 | 0.352
-2 | 0.368
-1 | 0.384
0 | 0.4
1 | 0.42
2 | 0.44
3 | 0.46
4 | 0.48
5 | 0.5
6 | 0.526
7 | 0.552
8 | 0.578
9 | 0.604
10 | 0.63
11 | 0.666
12 | 0.702
13 | 0.738
14 | 0.774
15 | 0.81
16 | 0.848
17 | 0.886
18 | 0.924
19 | 0.962
20 | 1
21 | 1.05
22 | 1.1
23 | 1.15
24 | 1.2
25 | 1.25
26 | 1.316
27 | 1.382
28 | 1.448
29 | 1.514
30 | 1.58
31 | 1.664
32 | 1.748
33 | 1.832
34 | 1.872
35 | 2
36 | 2.1
37 | 2.2
38 | 2.3
39 | 2.4
40 | 2.5
41 | 2.628
42 | 2.756
43 | 2.884
44 | 3.012
45 | 3.15
46 | 3.316
47 | 3.482
48 | 3.648
49 | 3.814
50 | 3.98
51 | 4.184
52 | 4.388
53 | 4.592
54 | 4.796
55 | 5
56 | 5.26
57 | 5.52
58 | 5.78
59 | 6.04
60 | 6.3
61 | 6.62
62 | 6.94
63 | 7.26
64 | 7.58
65 | 7.9
66 | 8.32
67 | 8.74
68 | 9.16
69 | 9.58
70 | 10
71 | 10.52
72 | 11.04
73 | 11.56
74 | 12.08
75 | 12.6
76 | 13.24
77 | 13.88
78 | 14.52
79 | 15.16
80 | 15.8
81 | 16.64
82 | 17.48
83 | 18.32
84 | 19.16
85 | 20
86 | 21.04
87 | 22.08
88 | 23.12
89 | 24.16
90 | 25.2
91 | 26.45
92 | 27.7
93 | 28.95
94 | 30.2
95 | 31.6
96 | 33.28
97 | 34.96
98 | 36.64
99 | 38.32
100 | 40
101 | 42.08
102 | 44.16
103 | 46.24
104 | 48.32
105 | 50.4
106 | 52.96
107 | 55.52
108 | 58.08
109 | 60.64
110 | 63.2

## Temp Conv
Temperature Conversion
°F | °C
-11.2 | -24
-9.4 | -23
-7.6 | -22
-5.8 | -21
-4 | -20
-2.2 | -19
-0.4 | -18
1.4 | -17
3.2 | -16
5 | -15
6.8 | -14
8.6 | -13
10.4 | -12
12.2 | -11
14 | -10
15.8 | -9
17.6 | -8
19.4 | -7
21.2 | -6
23 | -5
24.8 | -4
26.6 | -3
28.4 | -2
30.2 | -1
32 | 0
33.8 | 1
35.6 | 2
37.4 | 3
39.2 | 4
41 | 5
42.8 | 6
44.6 | 7
46.4 | 8
48.2 | 9
50 | 10
51.8 | 11
53.6 | 12
55.4 | 13
57.2 | 14
59 | 15
60.8 | 16
62.6 | 17
64.4 | 18
66.2 | 19
68 | 20
69.8 | 21
71.6 | 22
73.4 | 23
75.2 | 24
77 | 25
78.8 | 26
80.6 | 27
82.4 | 28
84.2 | 29
86 | 30
87.8 | 31
89.6 | 32
91.4 | 33
93.2 | 34
95 | 35
96.8 | 36
98.6 | 37
100.4 | 38
102.2 | 39
104 | 40
105.8 | 41
107.6 | 42
109.4 | 43
111.2 | 44
113 | 45
114.8 | 46
116.6 | 47
118.4 | 48
120.2 | 49
122 | 50
123.8 | 51
125.6 | 52
127.4 | 53
129.2 | 54
131 | 55
132.8 | 56
134.6 | 57
136.4 | 58
138.2 | 59
140 | 60
141.8 | 61
143.6 | 62
145.4 | 63
147.2 | 64
149 | 65
150.8 | 66
152.6 | 67
154.4 | 68
156.2 | 69
158 | 70
159.8 | 71
161.6 | 72
163.4 | 73
165.2 | 74
167 | 75
168.8 | 76
170.6 | 77
172.4 | 78
174.2 | 79
176 | 80
177.8 | 81
179.6 | 82
181.4 | 83
183.2 | 84
185 | 85
186.8 | 86
188.6 | 87
190.4 | 88
192.2 | 89
194 | 90
195.8 | 91
197.6 | 92
199.4 | 93
201.2 | 94
203 | 95
204.8 | 96
206.6 | 97
208.4 | 98
210.2 | 99
212 | 100
213.8 | 101
215.6 | 102
217.4 | 103
219.2 | 104
221 | 105
222.8 | 106
224.6 | 107
226.4 | 108
228.2 | 109
230 | 110

## Dropdowns
Visual & Mechanical Inspectiom Dropdown Options
Select One
Satisfactory
Unsatisfactory
Cleaned
See Comments
Not Applicable
Insulation Resistance Unit Answer Choices
kΩ | Kilo-Ohms
MΩ | Mega-Ohms
GΩ | Giga-Ohms
Insulation Resistance Test Voltages
250V
500V
1000V
2500V
5000V
Contact Resistance
μΩ | Micro-Ohms
mΩ | Milli-Ohms
Ω | Ohms
Dielectric Withstand Unit Answer Choices
μA | Mirco Amp
mA | Milli Amp
VLF Withstand Test Voltages
Cable Rating | Test voltage
5 | 10
8 | 13
15 | 21
20 | 26
25 | 32
28 | 36
30 | 38
35 | 44
46 | 57
69 | 84
Cable Size
#18
#16
#12
#10
#8
#6
#4
#2
#1
1/0
2/0
3/0
4/0
250
300
350
400
500
600
750
1000
Equipment Evaluation Result
PASS
FAIL
LIMITED SERVICE