## Test Sheet
| Customer | [17 empty] | Job # | [7 empty] | PASS
| Address | [17 empty] | Technicians
User
| Date | [5 empty] | Temp. |  |  | °F | -17.8 |  | °C | Humidity |  |  | % |  | Substation
| Identifier | [17 empty] | Eqpt. Location
Nameplate Data
| Manufacturer | [7 empty] | Catalog Number | [9 empty] | Serial Number
| KVA |  |  |  | / |  |  |  | Temp. Rise | [9 empty] | Impendance
|  |  | Voltages (V) | [5 empty] | Winding Connections | [6 empty] | Winding Material
| High Voltage |  | 480 |  | / | 277.1281 |  |  | Wye
| Low Voltage |  | 208 |  | / |  |  |  | Delta
| Tap Configuration |  |  | LV Winding 7 Positions
| Tap Position |  |  | 1 |  |  | 2 |  | 3 |  |  | 4 |  |  | 5 | [6 empty] | As Left:
| Tap Voltages |  |  | 218 |  |  | 213 |  | 208 |  |  | 203 |  |  | 198
Visual and Mechanical Inspection
| NETA Section | [24 empty] | Results
| 7.2.1.1.A.1 |  | Compare equipment nameplate data with drawings.
| 7.2.1.1.A.2 |  | Inspect physical and mechanical condition.
| 7.2.1.1.A.3 |  | Inspect anchorage, alignment, and grounding.
| 7.2.1.1.A.4 |  | Verify that resilient mounts are free and that any shipping brackets have been removed.
| 7.2.1.1.A.5 |  | Verify the unit is clean.
| 7.2.1.1.A.6 |  | Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method or in accordance with 7.2.1.1.B.1 (Low Resistance Ohmmeter).
| 7.2.1.1.A.7 |  | Verify that as-left tap connections are as specified.
| 7.2.1.1.A.8 |  | *Perform thermographic survey in accordance with Section 9.
Electrical - Insulation Resistance Tests
[10 empty] | Insulation Temperature (°F): | [9 empty] | Test Voltage (V): |  |  |  |  | 1000V
[10 empty] | Temperature Correction Factor: | [6 empty] | 0.176 |  |  | Test Duration: |  |  |  |  | 1 min
| Winding Under Test |  |  |  | Measured Values | [6 empty] | Temperature Corrected | [5 empty] | Units |  | Table 100.5 Criteria | [5 empty] | Results
[5 empty] | 0.5 Min. |  |  | 1 Min. |  |  |  | 0.5 Min. |  |  |  | 1 Min. |  |  |  | Value |  |  | Units
| Primary to Ground | [16 empty] | MΩ |  | ≥ | 500 |  | MΩ
| Secondary to Ground | [16 empty] | MΩ |  | ≥ | 500 |  | MΩ
| Primary to Secondary | [16 empty] | MΩ |  | ≥ | 500 |  | MΩ
[6 empty] | Calculated as: | [5 empty] | Pri to Gnd |  |  |  | Sec to Gnd |  | Pri to Sec |  |  | Criteria |  |  |  |  | Result
| Dielectric Absorption Ratio |  |  |  |  | 1 Min. / 0.5 Min. Values | [14 empty] | ≥ | 1
Electrical - Turns Ratio Tests
[10 empty] | Primary Winding |  |  | Measured Ratio (MR) |  |  | % Deviation from CR |  | Results
| Tap Under Test: |  |  |  |  | 3 | [14 empty] | Difference (%) between MR |  |  |  | Results
| HV Winding Voltage: |  |  |  |  | 277.1281 |  | V |  | H0-H1 |  |  | 1.3407 |  |  | -0.62696 |  | Fail
| LV Winding Voltage: |  |  |  |  | 208 |  | V |  | H0-H2 |  |  | 1.3414 |  |  | -0.67949 |  | Fail |  |  | 0.060044 |  |  |  | Pass
| Calculated Ratio (CR): |  |  |  |  | 1.3323 |  |  |  | H0-H3 |  |  | 1.3415 |  |  | -0.687 |  | Fail
Test Equipment Used
|  | Megohmmeter: | [12 empty] | Serial Number: | [8 empty] | AMP ID:
|  | TTR Test Set: | [12 empty] | Serial Number: | [8 empty] | AMP ID:
Comments: