## Test Sheet
| Customer | [15 empty] | Job # | [6 empty] | PASS
| Address | [15 empty] | Technicians
User
| Date |  |  | Temp. |  | 25 |  | °F | -3.9 |  | °C | Humidity |  |  | % |  | Substation
| Identifier | [15 empty] | Eqpt. Location
Nameplate Data
| Manufacturer | [5 empty] | Catalog Number | [9 empty] | Serial Number
| KVA |  | / |  |  |  | Temp. Rise | [9 empty] | Impendance
|  | Voltages (V) |  |  |  |  | Winding Connections | [5 empty] | Winding Material
| Primary |  | /
| Secondary |  | /
| Tap Position | 1 | 2 |  | 3 |  |  | 4 |  |  | 5 |  | 6 |  | 7 |  |  | Tap Position Left:
| Tap Voltages | [11 empty] | - |  | -
Indicator Gauge Values
| Oil Level |  |  |  |  | Oil Temperature (°C) | [6 empty] | 22 |  |  |  | Oil Temp. Range
| Tank Pressure |  |  |  |  | Winding Temperature (°C) | [10 empty] | Winding Temp. Range
Visual and Mechanical Inspection
| NETA Section | [21 empty] | Results
| 7.2.2.A.1 | Compare equipment nameplate data with drawings.
| 7.2.2.A.2 | Inspect physical and mechanical condition.
| 7.2.2.A.3 | Inspect impact recorder prior to unloading.
| 7.2.2.A.5 | Inspect anchorage, alignment, and grounding.
| 7.2.2.A.6 | Verify the presence of PCB content labeling.
| 7.2.2.A.7 | Verify removal of any shipping bracing after placement.
| 7.2.2.A.8 | Verify the bushings are clean.
| 7.2.2.A.9 | Verify that alarm, control, and trip settings on temperature and level indicators are as specified.
| 7.2.2.A.10 | Verify operation of alarm, control, and trip circuits from temperature and level indicators, pressure relief device, gas accumulator, and fault pressure relay.
| 7.2.2.A.11 | Verify that cooling fans and pumps operate correctly and have appropriate overcurrent protection.
| 7.2.2.A.12 | Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method or in accordance with 7.2.2.B.1. Torque values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.
| 7.2.2.A.13 | Verify correct liquid level in tanks and bushings.
| 7.2.2.A.14 | Verify valves are in the correct operating position.
| 7.2.2.A.15 | Verify that positive pressure is maintained on gas-blanketed transformers.
| 7.2.2.A.16 | Perform inspections and mechanical tests as recommended by the manufacturer.
| 7.2.2.A.17 | Test load tap-changer in accordance with Section 7.12.3.
| 7.2.2.A.18 | Verify presence of transformer surge arresters.
| 7.2.2.A.19 | Verify de-energized tap-changer position is left as specified.
Visual & Mechanical Inspection Comments:
Electrical - Insulation Resistance Tests
[21 empty] | TCF | 1.152
|  |  | Insulation Resistance Values | [12 empty] | Temperature Corrected Values
| Winding Under Test |  | Test Voltage |  |  | 0.5 Min. |  |  | 1 Min. |  |  | 10 Min. |  | Units |  | 0.5 Min. |  | 1 Min. |  |  | 10 Min. |  | Units
| Primary to Ground |  | 5000V | [10 empty] | MΩ | [8 empty] | MΩ
| Secondary to Ground |  | 1000V | [10 empty] | MΩ | [8 empty] | MΩ
| Primary to Secondary |  | 5000V | [10 empty] | MΩ | [8 empty] | MΩ
Primary to Secondary
[14 empty] | Primary |  |  | Secondary | [5 empty] | Acceptable
Dielectric Absorption : (Ratio of 1 Minute to 0.5 Minute Result )
Polarization Index : (Ratio of 10 Minute to 1 Minute Result )
Test Equipment Used
| Megohmmeter: | [8 empty] | Serial Number: | [8 empty] | AMP ID:
| TTR Test Set: | [8 empty] | Serial Number: | [8 empty] | AMP ID:
Comments:

## TCF
Insulation Correction Factors (20C)
Tempurature | Multiplier | Type of Value
-24 | 0.048 | Arbitrarily selected as a floor factor
-23 | 0.051 | Interpolated
-22 | 0.055 | Interpolated
-21 | 0.059 | Interpolated
-20 | 0.063 | Interpolated
-19 | 0.068 | Interpolated
-18 | 0.073 | Interpolated
-17 | 0.078 | Interpolated
-16 | 0.083 | Interpolated
-15 | 0.089 | Interpolated
-14 | 0.096 | Interpolated
-13 | 0.103 | Interpolated
-12 | 0.11 | Interpolated
-11 | 0.118 | Interpolated
-10 | 0.125 | NETA VALUE
-9 | 0.135 | Interpolated
-8 | 0.145 | Interpolated
-7 | 0.155 | Interpolated
-6 | 0.166 | Interpolated
-5 | 0.18 | NETA VALUE
-4 | 0.191 | Interpolated
-3 | 0.205 | Interpolated
-2 | 0.219 | Interpolated
-1 | 0.235 | Interpolated
0 | 0.25 | NETA VALUE
1 | 0.27 | Interpolated
2 | 0.289 | Interpolated
3 | 0.31 | Interpolated
4 | 0.332 | Interpolated
5 | 0.36 | NETA VALUE
6 | 0.381 | Interpolated
7 | 0.409 | Interpolated
8 | 0.438 | Interpolated
9 | 0.469 | Interpolated
10 | 0.5 | NETA VALUE
11 | 0.539 | Interpolated
12 | 0.577 | Interpolated
13 | 0.619 | Interpolated
14 | 0.663 | Interpolated
15 | 0.75 | NETA VALUE
16 | 0.761 | Interpolated
17 | 0.816 | Interpolated
18 | 0.874 | Interpolated
19 | 0.937 | Interpolated
20 | 1 | NETA VALUE
21 | 1.075 | Interpolated
22 | 1.152 | Interpolated
23 | 1.235 | Interpolated
24 | 1.323 | Interpolated
25 | 1.4 | NETA VALUE
26 | 1.519 | Interpolated
27 | 1.628 | Interpolated
28 | 1.745 | Interpolated
29 | 1.869 | Interpolated
30 | 1.98 | NETA VALUE
31 | 2.146 | Interpolated
32 | 2.3 | Interpolated
33 | 2.464 | Interpolated
34 | 2.641 | Interpolated
35 | 2.8 | NETA VALUE
36 | 3.032 | Interpolated
37 | 3.249 | Interpolated
38 | 3.482 | Interpolated
39 | 3.731 | Interpolated
40 | 3.95 | NETA VALUE
41 | 4.284 | Interpolated
42 | 4.59 | Interpolated
43 | 4.918 | Interpolated
44 | 5.27 | Interpolated
45 | 5.6 | NETA VALUE
46 | 6.051 | Interpolated
47 | 6.484 | Interpolated
48 | 6.948 | Interpolated
49 | 7.445 | Interpolated
50 | 7.85 | NETA VALUE
51 | 8.549 | Interpolated
52 | 9.16 | Interpolated
53 | 9.816 | Interpolated
54 | 10.518 | Interpolated
55 | 11.2 | NETA VALUE
56 | 12.077 | Interpolated
57 | 12.941 | Interpolated
58 | 13.866 | Interpolated
59 | 14.859 | Interpolated
60 | 15.85 | NETA VALUE
61 | 17.061 | Interpolated
62 | 18.281 | Interpolated
63 | 19.589 | Interpolated
64 | 20.991 | Interpolated
65 | 22.4 | NETA VALUE
66 | 24.101 | Interpolated
67 | 25.826 | Interpolated
68 | 27.673 | Interpolated
69 | 29.653 | Interpolated
70 | 31.75 | NETA VALUE
71 | 34.048 | Interpolated
72 | 36.484 | Interpolated
73 | 39.094 | Interpolated
74 | 41.891 | Interpolated
75 | 44.7 | NETA VALUE
76 | 48.1 | Interpolated
77 | 51.541 | Interpolated
78 | 55.228 | Interpolated
79 | 59.179 | Interpolated
80 | 63.5 | NETA VALUE
81 | 67.95 | Interpolated
82 | 72.811 | Interpolated
83 | 78.021 | Interpolated
84 | 83.603 | Interpolated
85 | 89.789 | NETA VALUE
86 | 95.993 | Interpolated
87 | 102.861 | Interpolated
88 | 110.219 | Interpolated
89 | 118.105 | Interpolated
90 | 127 | NETA VALUE
91 | 135.609 | Interpolated
92 | 145.311 | Interpolated
93 | 155.707 | Interpolated
94 | 166.846 | Interpolated
95 | 180 | NETA VALUE
96 | 191.574 | Interpolated
97 | 205.28 | Interpolated
98 | 219.966 | Interpolated
99 | 235.703 | Interpolated
100 | 245 | NETA VALUE
101 | 270.636 | Interpolated
102 | 289.998 | Interpolated
103 | 310.745 | Interpolated
104 | 332.977 | Interpolated
105 | 359.15 | NETA VALUE
106 | 382.326 | Interpolated
107 | 409.679 | Interpolated
108 | 438.989 | Interpolated
109 | 470.395 | Interpolated
110 | 509 | NETA VALUE