## Test Sheet
| Customer | [19 empty] | Job # | [7 empty] | PASS
| Address | [19 empty] | Technicians
User
| Date |  |  |  |  | Temp. |  |  |  | °F | -17.8 |  | °C | Humidity |  |  |  |  | % |  | Substation
| Identifier | [19 empty] | Eqpt. Location
Nameplate Data
| Manufacturer | [7 empty] | Cat./Model No. | [9 empty] | Serial Number | [7 empty] | Year Mfd.
| Rated KVA |  |  |  | Power Factor | [6 empty] | Rated kW | [6 empty] | HP |  |  |  | RPM
| Voltages (V) |  | / |  |  |  | Current Rating (A) | [7 empty] | Frequency (Hz) | [6 empty] | Connections
Visual and Mechanical Inspection
| NETA Section | [25 empty] | Results
| 7.22.1.A.1 | Compare equipment nameplate data with drawings.
| 7.22.1.A.2 | Inspect physical and mechanical condition.
| 7.22.1.A.3 | Inspect anchorage, alignment, and grounding.
| 7.22.1.A.4 | Verify the unit is clean.
Electrical - Insulation Resistance Tests
| Insulation Type: | [6 empty] | Thermosetting |  |  |  |  | Test method: |  |  |  | Single test from all phases to ground
Insulation Temperature (°C):
| Temperature Correction Factor to 40°C : | [6 empty] | 0.1324
[13 empty] | Measured Values | [8 empty] | Temperature Corrected Values
| Winding Under Test | [7 empty] | Test Voltage |  |  |  | 30 Sec. |  |  | 1 Min. |  |  | 10 Min. |  |  | 30. Sec. |  | 1 Min. |  | 10 Min. |  |  | Units
A-Phase to Ground, B- & C-phases Grounded
B-Phase to Ground, A- & C-phases Grounded
C-Phase to Ground, A- & B-phases Grounded
A-, B-, & C-Phase (shorted) to Ground
|  |  |  | Calculated as: | [9 empty] | A Phase |  |  |  | B Phase |  |  |  | C Phase |  |  | Phases to Gnd |  |  | Result
| Dielectric Absorption |  |  | Ratio of 1 Min. to 30 Sec. Results
| Polarization Index |  |  | Ratio of 10 Min. to 1 Min. Results
Compare temperature corrected values to IEEE-43 & NETA minimum insulation resistances:
Test Equipment Used
| Megohmmeter: | [6 empty] | Serial Number: | [11 empty] | AMP ID: | [5 empty] | Cal Date:
Comments: