## Test Sheet
Customer | [21 empty] | Job # | [7 empty] | PASS
Address | [21 empty] | Technicians
User
Date | [7 empty] | Temp. |  | 89 |  | °F | 31.7 |  | °C | Humidity |  |  |  |  | % | Substation
Identifier | [21 empty] | Eqpt. Location
Nameplate Data
[5 empty] | Manufacturer | [13 empty] | Rated Voltage (V) |  |  |  |  | 480
[5 empty] | Catalog No. | [13 empty] | System Voltage (V)
[5 empty] | Serial Number | [13 empty] | Rated Current (A)
[5 empty] | Series | [13 empty] | AIC Rating (kA)
[5 empty] | Type | [13 empty] | Phase Configuration
Visual and Mechanical Inspection
| NETA Section | [26 empty] | Results
| 7.4.A.1 |  |  | Compare equipment nameplate data with drawings.
| 7.4.A.2 |  |  | Inspect physical, electrical, and mechanical condition.
| 7.4.A.3 |  |  | Inspect anchorage, alignment, grounding, and required area clearances.
| 7.4.A.4 |  |  | Verify correct connection in accordance with single-line diagram.
| 7.4.A.5 |  |  | Verify tightness of accessible bolted electrical connections and bus joints by calibrated torque-wrench method or in accordance with 7.4.B.1.
| 7.4.A.6 |  |  | Confirm physical orientation in accordance with manufacturer’s labels to ensure adequate cooling.
| 7.4.A.7 |  |  | Verify weep or drain plugs are in accordance with manufacturer’s published data.
| 7.4.A.8 |  |  | Verify correct installation of joint shield.
| 7.4.A.9 |  |  | Verify ventilating openings are clean.
| 7.4.A.10 |  |  | *Perform thermographic survey in accordance with Section 9.
Electrical - Bus Resistance Tests
| Bus Resistance | [23 empty] | Value Deviation |  | Criteria |  | Results
| Bus Section |  |  |  |  | A-Phase |  | B-Phase |  |  | C-Phase |  |  | Neutral |  |  | Ground |  |  | Units
| End to End |  |  |  |  | 52 |  | 48 |  |  | 56 |  |  | 24 |  |  | 34 |  |  | µΩ |  | Phase: |  |  | 16.67% |  | <50% |  | PASS
| JP1 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
| JP2 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
| JP3 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
| JP4 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
| JP5 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
| JP6 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
| JP7 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
| JP8 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
| JP9 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
| JP10 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
| JP11 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
| JP12 | [20 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
[22 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
[22 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
[22 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
[22 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
[22 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
[22 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
[22 empty] | Phase: |  |  | N/A |  | N/A |  | N/A
Electrical - Insulation Resistance Tests
[15 empty] | Insulation Temperature (°F): | [6 empty] | 80 |  |  |  | Test Voltage: |  | 5000V
[15 empty] | Temp. Correction Factor: | [6 empty] | 1.363 |  |  |  | Test Duration: |  | 1 min.
Measured Values
| A-G |  | B-G |  |  | C-G |  | A-B |  |  | B-C |  |  | C-A |  |  | A-N |  |  | B-N |  | C-N |  |  | Units
| > | 2200 | > | 2300 |  | > | 2400 | > | 2500 |  | > | 2600 |  | > | 2700 |  | > | 2800 |  | > | 2900 | > | 3000 |  | MΩ
Temperature Corrected Values
| A-G |  | B-G |  |  | C-G |  | A-B |  |  | B-C |  |  | C-A |  |  | A-N |  |  | B-N |  | C-N |  |  | Units
| > | 2998.6 | > | 3134.9 |  | > | 3271.2 | > | 3407.5 |  | > | 3543.8 |  | > | 3680.1 |  | > | 3816.4 |  | > | 3952.7 | > | 4089 |  | MΩ
[6 empty] | Value |  |  | Units
| Table 100.1 Criteria: |  |  |  |  | ≥ | 100 |  | MΩ |  |  |  | Overall Result: |  |  |  |  | PASS
Test Equipment Used
|  | Low Resistance Ohmmeter: | [12 empty] | Serial Number: | [10 empty] | AMP ID:
|  | Megohmmeter: | [12 empty] | Serial Number: | [10 empty] | AMP ID:
Comments: