## Test Sheet
| Customer | [20 empty] | Job # | [8 empty] | PASS
| Address | [20 empty] | Technicians
| User | [20 empty] | Substation
| Date | [8 empty] | Temp. |  |  |  | °F | -17.8 |  | °C | Humidity |  |  | % | Eqpt. Identifer
| Breaker Identifier | [20 empty] | Circuit / Cell No.
Nameplate Data
| Manufacturer | [11 empty] | Frame Size (A) | [9 empty] | Curve No.
| Catalog Number | [11 empty] | Rating Plug (A) | [9 empty] | Operation |  |  |  |  | Over-Center Handle
| Serial Number | [11 empty] | Rated Voltage (V) | [5 empty] | 480 |  |  |  | Mounting
| Breaker Type | [11 empty] | Operating Voltage (V) | [5 empty] | 480 |  |  |  | Zone Interlock
| Trip Unit Type | [11 empty] | I.C. Rating (kA) | [9 empty] | Thermal Memory
Visual and Mechanical Inspection
| NETA Section | [28 empty] | Results
| 7.6.1.1.1.A.1 |  |  |  | Compare equipment nameplate data with drawings.
| 7.6.1.1.1.A.2 |  |  |  | Inspect physical and mechanical condition.
| 7.6.1.1.1.A.3 |  |  |  | Verify the unit is clean.
| 7.6.1.1.1.A.4 |  |  |  | Operate the circuit breaker to ensure smooth operation.
| 7.6.1.1.1.A.5 |  |  |  | Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method. Torque values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.
| 7.6.1.1.1.A.6 |  |  |  | Perform adjustments for final protective device settings in accordance with the coordination study.
| 7.6.1.1.1.A.7 |  |  |  | *Perform thermographic survey in accordance with Section 9.
Device Settings
| Trip Type: |  |  |  |  | LSIG |  |  |  | Settings As Found | [11 empty] | Settings As Left
[10 empty] | Function |  |  |  |  | Setting |  |  | Delay |  | I2t |  | Function |  |  |  |  | Setting |  |  | Delay |  | I2t
| Coordination Study | [8 empty] | Long Time | [11 empty] | Long Time
| No./ID. | [8 empty] | Short Time | [11 empty] | Short Time
| Rev. | [8 empty] | Instantaneous | [11 empty] | Instantaneous
| Date | [8 empty] | Ground Fault | [11 empty] | Ground Fault
Electrical Tests - Contact/Pole Resistance
| Resistance Measurements | [13 empty] | Value Deviation | [6 empty] | Result
| Pole 1 |  |  |  | Pole 2 |  |  |  | Pole 3 |  |  | Units |  |  | Measured |  |  |  | Criteria |  |  | -
[12 empty] | µΩ |  |  | - |  |  |  | <50%
Electrical Tests - Insulation Resistance
[16 empty] | Insulation Temperature (°F): | [10 empty] | Test Voltage (V): |  |  |  | 1000
[16 empty] | Temperature Correction Factor: | [6 empty] | 0.176 |  |  |  | Test Duration: |  |  |  | 1 min
| Test Points |  |  |  | Breaker Position |  |  | Measured Values | [7 empty] | Temperature Corrected | [9 empty] | Table 100.1 Criteria |  |  |  |  | Results
[8 empty] | P1 (P1-P2) |  | P2 (P2-P3) |  |  | P3 (P3-P1) |  |  | P1 (P1-P2) |  |  | P2 (P2-P3) |  | P3 (P3-P1) |  | Units |  |  | Value |  |  | Units
| Pole to Pole |  |  |  | Closed | [17 empty] | MΩ |  |  | ≥ | 100 |  | MΩ |  | -
| Pole to Frame | [21 empty] | MΩ |  |  | ≥ | 100 |  | MΩ |  | -
| Line to Load |  |  |  | Open | [17 empty] | MΩ |  |  | > | 100 |  | MΩ |  | -
Electrical Tests - Current Sensing
Tested Settings
|  | Test Type | [13 empty] | Setting |  |  | Delay |  | I2t |  |  | LTPU Indicator?
|  | Secondary Injection | [8 empty] | Long Time | [12 empty] | Yes
Short Time
Instantaneous
Ground Fault
| Function |  |  | Setting Amperes |  |  | Multiplier % |  |  | Test Amperes |  |  | Tolerance | [5 empty] | Pole 1 |  |  | Pole 2 |  |  |  |  | Pole 3 |  |  |  | Results
[7 empty] | Tolerance | [5 empty] | Min |  |  | Max
| LTD | [5 empty] | 300% | [13 empty] | sec. |  |  |  | sec. |  |  |  |  | sec.
| LTPU | [5 empty] | -10% |  | 10% | [11 empty] | A |  |  |  | A |  |  |  |  | A
| STD | [5 empty] | 110% | [13 empty] | sec. |  |  |  | sec. |  |  |  |  | sec.
| STPU | [5 empty] | -10% |  | 10% | [11 empty] | A |  |  |  | A |  |  |  |  | A
| INST-D | [5 empty] | 110% | [13 empty] | sec. |  |  |  | sec. |  |  |  |  | sec.
| INST-PU | [5 empty] | -20% |  | 20% | [11 empty] | A |  |  |  | A |  |  |  |  | A
| GFD | [5 empty] | 110% | [13 empty] | sec. |  |  |  | sec. |  |  |  |  | sec.
| GFPU | [5 empty] | -15% |  | 15% | [11 empty] | A |  |  |  | A |  |  |  |  | A
Test Equipment Used
|  | Digital Low-Resistance Ohmmeter: | [15 empty] | Serial Number: | [9 empty] | AMP ID:
|  |  |  | Megohmmeter: | [13 empty] | Serial Number: | [9 empty] | AMP ID:
|  |  |  | Primary Injection Test Set: | [13 empty] | Serial Number: | [9 empty] | AMP ID:
Comments:
Function Legend:
| LTD |  |  | Long Time Delay | [5 empty] | INST-D |  |  | Instantaneous Delay | [6 empty] | Thermal |  | Overload protection element
| LTPU |  |  | Long Time Pick-up | [5 empty] | INST-PU |  |  | Instantaneous Pick-up | [6 empty] | Magnetic |  | Short circuit protection element
| STD |  |  | Short Time Delay | [5 empty] | GFD |  |  | Ground Fault Delay
| STPU |  |  | Short Time Pick-up | [5 empty] | GFPU |  |  | Ground Fault Pick-up
Trip Type Legend:
| LI |  | Long-Time, Instantaneous | [13 empty] | TMF |  | Fixed Thermal, Fixed Magnetic
| LS |  | Long Time, Short Time | [13 empty] | TMD |  | AdjustableThermal, Fixed Magnetic
| LSI |  | Long Time, Short Time, | [13 empty] | TMA |  | Fixed Thermal, Adjustable Magnetic
| LIG |  | Long Time, Instantaneous, Ground Fault | [13 empty] | TF |  | Fixed Thermal
| LSG |  | Long Time, Short Time, Ground Fault | [13 empty] | TA |  | Adjustable Thermal
| LSIG |  | Long Time, Short Time, Instantaneous, Ground Fault | [13 empty] | MF |  | Fixed Magnetic
| G |  | Ground Fault | [13 empty] | MA |  | Adjustable Magnetic