## Test Sheet
Customer | [20 empty] | Job # | [8 empty] | PASS
Address | [20 empty] | Technicians
User
Date | [6 empty] | Temp. |  | 89 |  | °F | 31.7 |  | °C | Humidity |  |  |  |  | % | Substation
Identifier | [20 empty] | Eqpt. Location
Nameplate Data
|  |  |  | Manufacturer | [13 empty] | Rated Voltage (V) |  |  |  |  | 34500
|  |  |  | Catalog No. | [13 empty] | System Voltage (V)
|  |  |  | Serial Number | [13 empty] | Rated Current (A)
|  |  |  | Series | [13 empty] | AIC Rating (kA)
|  |  |  | Type | [13 empty] | Phase Configuration
Visual and Mechanical Inspection
| NETA Section | [26 empty] | Results
| 7.1.1.A.1 |  | Compare equipment nameplate data with drawings.
| 7.1.1.A.2 |  | Inspect physical, electrical, and mechanical condition.
| 7.1.1.A.3 |  | Inspect anchorage, alignment, grounding, and required area clearances.
| 7.1.1.A.4 |  | Verify the unit is clean and all shipping bracing, loose parts, and documentation shipped inside cubicles have been removed.
| 7.1.1.A.5 |  | Compare mimic diagram and device labeling with drawings.
| 7.1.1.A.6 |  | Verify that fuse and circuit breaker sizes and types correspond to drawings and coordination study as well as to the circuit breaker address for microprocessor-communication packages.
| 7.1.1.A.7 |  | Verify that current and voltage transformer ratios correspond to drawings.
| 7.1.1.A.8 |  | Verify that wiring connections are tight and that wiring is secure to prevent damage during routine operation of moving parts.
| 7.1.1.A.9 |  | Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method or in accordance with 7.1.1.B.1. Torque values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.
| 7.1.1.A.10 |  | Confirm correct operation and sequencing of electrical and mechanical interlock systems. - Attempt closure on locked-open devices. Attempt to open locked-closed devices. - Make key exchange with all devices included in the interlock scheme.
| 7.1.1.A.11 |  | Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.
| 7.1.1.A.12 |  | Inspect insulators for evidence of physical damage or contaminated surfaces.
| 7.1.1.A.13 |  | Verify correct barrier and shutter installation and operation.
| 7.1.1.A.14 |  | Exercise all active components.
| 7.1.1.A.15 |  | Inspect mechanical indicating devices for correct operation.
| 7.1.1.A.16 |  | Verify that filters are in place and vents are clear.
| 7.1.1.A.17 |  | Perform visual and mechanical inspection of instrument transformers in accordance with Section 7.10.
| 7.1.1.A.18 |  | Perform visual and mechanical inspection of surge arresters in accordance with Section 7.19.
| 7.1.1.A.19 |  | Inspect control power transformers.
| 7.1.1.A.20 |  | *Perform thermographic survey in accordance with Section 9.
Electrical - Contact Resistance Tests
| Contact Resistance | [22 empty] | Value Deviation |  | Criteria |  |  | Results
| Bus Section |  |  |  | A-Phase |  | B-Phase |  |  | C-Phase |  |  | Neutral |  |  | Ground |  |  | Units
| Section 1 to Section 2 |  |  |  | 52 |  | 48 |  |  | 56 |  |  | N/A |  |  | N/A |  |  | µΩ |  | Phase: |  |  | 16.67% |  | <50% |  |  | PASS
| Section 2 to Section 3 | [11 empty] | N/A |  |  | N/A |  |  |  |  | Phase: |  |  | N/A |  | N/A |  |  | N/A
| Section 3 to Section 4 | [19 empty] | Phase: |  |  | N/A |  | N/A |  |  | N/A
| Section 4 to Section 5 | [19 empty] | Phase: |  |  | N/A |  | N/A |  |  | N/A
[21 empty] | Phase: |  |  | N/A |  | N/A |  |  | N/A
[21 empty] | Phase: |  |  | N/A |  | N/A |  |  | N/A
[21 empty] | Neutral : |  |  | N/A |  | N/A |  |  | N/A
[21 empty] | Ground: |  |  | N/A |  | N/A |  |  | N/A
Electrical - Insulation Resistance Tests
[14 empty] | Insulation Temperature (°F): | [6 empty] | 80 |  |  |  | Test Voltage: |  |  | 5000V
[14 empty] | Temp. Correction Factor: | [6 empty] | 1.363 |  |  |  | Test Duration: |  |  | 1 min.
Measured Values
| Bus Section |  |  |  | A-G |  | B-G |  |  | C-G |  |  | A-B |  |  | B-C |  |  | C-A |  | A-N |  |  | B-N |  | C-N |  |  | Units
| Section 1 |  |  |  | > | 2200 | > | 2300 |  | > | 2400 |  | > | 2500 |  | > | 2600 |  | > | 2700 | > | 2800 |  | > | 2900 | > | 3000 |  | MΩ
| Section 2 | [27 empty] | MΩ
| Section 3 | [27 empty] | MΩ
| Section 4 | [27 empty] | MΩ
| Section 5 | [27 empty] | MΩ
Temperature Corrected Values
| Bus Section |  |  |  | A-G |  | B-G |  |  | C-G |  |  | A-B |  |  | B-C |  |  | C-A |  | A-N |  |  | B-N |  | C-N |  |  | Units
| Section 1 |  |  |  | > | 2998.6 | > | 3134.9 |  | > | 3271.2 |  | > | 3407.5 |  | > | 3543.8 |  | > | 3680.1 | > | 3816.4 |  | > | 3952.7 | > | 4089 |  | MΩ
| Section 2 | [27 empty] | MΩ
| Section 3 | [27 empty] | MΩ
| Section 4 | [27 empty] | MΩ
| Section 5 | [27 empty] | MΩ
[18 empty] | Value |  |  | Units
[12 empty] | Table 100.1 Criteria: | [5 empty] | ≥ | 100000 |  | MΩ |  |  | Overall Result: |  |  |  | PASS
Electrical - Dielectric Withstand Tests
| Bus Section |  |  |  | A-G |  | B-G |  |  | C-G |  |  | Units |  |  | Results | [7 empty] | Test Voltage: |  |  | 2.3 kVDC
| Section 1 | [11 empty] | μA |  |  | PASS | [7 empty] | Test Duration: |  |  | 1 min.
| Section 2 | [11 empty] | μA |  |  | PASS
| Section 3 | [11 empty] | μA |  |  | PASS
| Section 4 | [11 empty] | μA |  |  | PASS
| Section 5 | [11 empty] | μA |  |  | PASS
Test Equipment Used
|  | Low Resistance Ohmmeter: | [11 empty] | Serial Number: | [10 empty] | AMP ID:
|  | Megohmmeter: | [11 empty] | Serial Number: | [10 empty] | AMP ID:
[5 empty] | Hipot: | [8 empty] | Serial Number: | [10 empty] | AMP ID:
Comments: