## Test Sheet
Customer | [16 empty] | Job # | [6 empty] | PASS
Address | [16 empty] | Technicians
User
Date | [6 empty] | Temp. |  | °F | -17.8 |  | °C | Humidity |  |  | % | Substation
Identifier | [16 empty] | Eqpt. Location
Nameplate Data
[5 empty] | Manufacturer | [9 empty] | Rated Voltage (V)
[5 empty] | Catalog No. | [9 empty] | Operating Voltage (V)
[5 empty] | Serial Number | [9 empty] | Rated Current (A)
[5 empty] | Series | [9 empty] | AIC Rating (kA)
[5 empty] | Type | [9 empty] | Phase Configuration
Visual and Mechanical Inspection
| NETA Section | [20 empty] | Results
| 7.1.2.A.1 |  |  | Compare equipment nameplate data with drawings.
| 7.1.2.A.2 |  |  | Inspect physical, electrical, and mechanical condition.
| 7.1.2.A.3 |  |  | Inspect anchorage, alignment, grounding, bonding, and required area clearances.
| 7.1.2.A.4 |  |  | Verify the unit is clean and all shipping bracing and loose parts have been removed.
| 7.1.2.A.5 |  |  | Verify that fuse and circuit breaker sizes and types correspond to drawings and coordination study.
| 7.1.2.A.6 |  |  | Verify that wiring connections are tight, and that wiring is secure to prevent damage during routine operation of moving parts.
| 7.1.2.A.7 |  |  | Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method. Torque values shall be in accordance with manufacturer’s published data. In the absence of manufacturer's data, use Table 100.12.
| 7.1.2.A.8 |  |  | Inspect insulators for evidence of physical damage or contaminated surfaces.
| 7.1.2.A.9 |  |  | Verify correct barrier installation.
| 7.1.2.A.10 |  |  | Perform visual and mechanical inspection on surge protective devices.
| 7.1.2.A.11 |  |  | Exercise all active components.
| 7.1.2.A.12 |  |  | *Perform thermographic survey in accordance with Section 9
Electrical - Insulation Resistance Tests
[11 empty] | Insulation Temperature (°F): | [7 empty] | Test Voltage (V):
[11 empty] | Temperature Correction Factor: | [5 empty] | 0.176 |  | Test Duration: |  |  |  | 1 min
|  | Test Points |  |  |  | Measured Values |  |  |  |  | Temp. Corrected Values | [5 empty] | Units | Table 100.1 Criteria |  |  |  |  | Results
[6 empty] | P1 (P1-P2) | P2 (P2-P3) | P3 (P3-P1) |  |  | P1 (P1-P2) |  |  | P2 (P2-P3) | P3 (P3-P1) |  |  | Value |  |  | Units
|  | Phase to Phase | [14 empty] | MΩ | ≥ |  |  | MΩ |  | -
|  | Phase to Ground | [14 empty] | MΩ | ≥ |  |  | MΩ |  | -
|  | Phase to Neutral | [14 empty] | MΩ | > |  |  | MΩ |  | -
Electrical - Contact Resistance Test for Torque Verification
[13 empty] | Performing Torque Verification using Low-Resistance Ohmmeter? | [10 empty] | Yes
|  | Resistance Measurements | [14 empty] | Phase Value Deviation | [5 empty] | Result
|  | Pole 1 |  |  | Pole 2 |  | Pole 3 |  | Neutral |  |  |  | Ground |  | Units |  | Measured |  | Criteria
[15 empty] | µΩ |  | - |  | <50% |  |  |  | -
Test Equipment Used
|  |  | Torque Wrench: | [9 empty] | Serial Number: | [6 empty] | AMP ID:
|  |  | Megohmmeter: | [9 empty] | Serial Number: | [6 empty] | AMP ID:
|  |  | Low Resistance Ohmmeter: | [9 empty] | Serial Number: | [6 empty] | AMP ID:
Comments: