## Test Sheet
| Customer | Toyota Motor Manufacturing Alabama | [18 empty] | Job # |  |  |  |  | 26097 |  |  |  | PASS
| Address | 1 Cottonvalley Dr NW, Huntsville, AL 35810,United States | [18 empty] | Technicians |  |  |  |  | RM/HG
| User | Toyota Motor Manufacturing Alabama
| Date | 2026-07-11 |  |  |  | Temp. |  | 82 |  | °F | 27 |  | °C |  | TCF |  | 1.382 |  |  |  | Substation |  |  |  |  | SUB 5A
| Identifier | BD-5A1 2GR CRANK | [11 empty] | Humidity |  |  |  | 66 | % |  | Eqpt. Location |  |  |  |  | SUB 5
Nameplate Data
| Manufacturer |  | Square D | [5 empty] | I.C. Rating (kA) | [5 empty] | 65 | [6 empty] | Operation |  |  |  |  | Manual
| Catalog Number |  | WAEBR64ASXFXXXXA | [5 empty] | Trip Unit Type | [5 empty] | Micrologic 6.0 P | [6 empty] | Mounting |  |  |  |  | Draw-out
| Serial Number |  | 085224035902 | [5 empty] | Rating Plug (A) | [5 empty] | 1200 | [6 empty] | Zone Interlock |  |  |  |  | N/A
| Type |  | NW 16 H1 | [5 empty] | Curve No. | [5 empty] | N/A | [6 empty] | Thermal Memory |  |  |  |  | Simulated
| Frame Size (A) |  | 1600 | [5 empty] | Charge Motor Voltage | [5 empty] | N/A
Visual and Mechanical Inspection
| NETA Section | [27 empty] | Results
| 7.6.1.2.A.1 | Compare equipment nameplate data with drawings and specifications. | [26 empty] | Satisfactory
| 7.6.1.2.A.2 | Inspect physical and mechanical condition. | [26 empty] | Satisfactory
| 7.6.1.2.A.3 | Inspect anchorage and alignment. | [26 empty] | Not Applicable
| 7.6.1.2.A.4 | Verify that all maintenance devices are available for servicing and operating the breaker. | [26 empty] | Satisfactory
| 7.6.1.2.A.5 | Verify the unit is clean. | [26 empty] | Cleaned
| 7.6.1.2.A.6 | Verify the arc chutes are intact. | [26 empty] | Satisfactory
| 7.6.1.2.A.7 | Inspect moving and stationary contacts for condition and alignment. | [26 empty] | Satisfactory
| 7.6.1.2.A.8 | Verify that primary and secondary contact wipe and other dimensions vital to satisfactory operation of the breaker are correct. | [26 empty] | Satisfactory
| 7.6.1.2.A.9 | Perform all mechanical operator and contact alignment tests on both the breaker and its operating mechanism in accordance with manufacturer’s published data. | [26 empty] | Satisfactory
| 7.6.1.2.A.10.1 | Use of a low-resistance ohmmeter in accordance with Section 7.6.1.2.B.1. | [26 empty] | Satisfactory
| 7.6.1.2.A.11 | Verify cell fit and element alignment. | [26 empty] | Not Applicable
| 7.6.1.2.A.12 | Verify racking mechanism operation. | [26 empty] | Not Applicable
| 7.6.1.2.A.13 | Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces. | [26 empty] | Satisfactory
| 7.6.1.2.A.14 | Perform adjustments for final protective device settings in accordance with coordination study provided by end user. | [26 empty] | Not Applicable
Device Settings
|  |  | Settings As Found | [13 empty] | Settings As Left
[7 empty] | Setting |  |  | Delay |  |  | I2t | [8 empty] | Setting |  |  | Delay |  |  | I2t
|  |  | Long Time |  |  |  | 1 |  |  | 16 | [6 empty] | Long Time |  |  |  |  | 1 |  |  | 16
|  |  | Short Time |  |  |  | 5 |  |  | 0.1 |  |  | Off |  |  |  | Short Time |  |  |  |  | 5 |  |  | 0.1 |  |  | Off
|  |  | Instantaneous |  |  |  | 6 | [9 empty] | Instantaneous |  |  |  |  | 6
|  |  | Ground Fault |  |  |  | H |  |  | 0.2 |  |  | Off |  |  |  | Ground Fault |  |  |  |  | H |  |  | 0.2 |  |  | Off
Electrical Tests - Contact/Pole Resistance
Contact Resistance
[5 empty] | P1 | [5 empty] | P2 | [5 empty] | P3 | [5 empty] | Units
[5 empty] | 13 | [5 empty] | 13 | [5 empty] | 11 | [5 empty] | μΩ
Electrical Tests - Insulation Resistance
|  | Test Voltage |  |  | 1000V |  |  |  | Measured Values | [8 empty] | Temperature Corrected
[9 empty] | P1 (P1-P2) |  |  | P2 (P2-P3) |  |  | P3 (P3-P1) |  |  | P1 (P1-P2) |  |  | P2 (P2-P3) |  |  | P3 (P3-P1) |  |  | Units
|  | Pole to Pole |  |  |  | Closed |  |  | >2200 |  |  | >2200 |  |  | >2200 |  |  | >2200 |  |  | >2200 |  |  | >2200 |  |  | MΩ
|  | Pole to Frame | [6 empty] | >2200 |  |  | >2200 |  |  | >2200 |  |  | >2200 |  |  | >2200 |  |  | >2200 |  |  | MΩ
|  | Line to Load |  |  |  | Open |  |  | >2200 |  |  | >2200 |  |  | >2200 |  |  | >2200 |  |  | >2200 |  |  | >2200 |  |  | kΩ
Electrical Tests - Secondary Injection
Tested Settings
[13 empty] | Setting |  |  | Delay |  |  | I2t
[8 empty] | Long Time |  |  |  |  | 1 |  |  | 16
[8 empty] | Short Time |  |  |  |  | 5 |  |  | 0.1 |  |  | Off
[8 empty] | Instantaneous |  |  |  |  | 6
[8 empty] | Ground Fault |  |  |  |  | H |  |  | 0.2 |  |  | Off
Secondary Injection
|  |  |  | Function |  |  |  |  | Rated Amperes |  |  | Test Amperes |  |  | Results
[15 empty] | Trip |  |  |  | Units |  |  | Pass/Fail
|  |  |  | Long Time |  |  |  |  | 1200 |  |  | 4400 |  |  | 38.553 |  |  |  | sec. |  |  | Pass
|  |  |  | Short Time |  |  |  |  | 6000 |  |  | 6600 |  |  | 0.131 |  |  |  | sec. |  |  | Pass
|  |  |  | Instantaneous |  |  |  |  | 7200 |  |  | 9000 |  |  | 0.043 |  |  |  | sec. |  |  | Pass
|  |  |  | Ground Fault |  |  |  |  | 1000 |  |  | 2160 |  |  | 0.159 |  |  |  | sec. |  |  | Pass
Electrical Tests - Primar Verification
Primary Confirmation
[12 empty] | P1 |  |  |  | P2 |  |  |  | P3
[5 empty] | Test Current (A) | [6 empty] | 100 |  |  |  | 100 |  |  |  | 100
[5 empty] | Measured Current (A) | [6 empty] | 105 |  |  |  | 101 |  |  |  | 101
Test Equipment Used
| Megohmmeter: |  |  |  | Fluke 1587 | [6 empty] | Serial Number: |  |  |  |  | 67590137 | [6 empty] | AMP ID: |  |  | 1-213
| Low-Resistance Ohmmeter: |  |  |  | Megger DLRO10HD | [6 empty] | Serial Number: |  |  |  |  | 101339243 | [6 empty] | AMP ID: |  |  | 1-385
| Secondary Injection Test Set: |  |  |  | SQUARE D S33595 | [6 empty] | Serial Number: |  |  |  |  | B0032216 | [6 empty] | AMP ID: |  |  | N/A
Comments:

## TCF
Insulation Correction Factors (20C)
Tempurature | Multiplier
-24 | 0.054
-23 | 0.068
-22 | 0.082
-21 | 0.096
-20 | 0.11
-19 | 0.124
-18 | 0.138
-17 | 0.152
-16 | 0.166
-15 | 0.18
-14 | 0.194
-13 | 0.208
-12 | 0.222
-11 | 0.236
-10 | 0.25
-9 | 0.264
-8 | 0.278
-7 | 0.292
-6 | 0.306
-5 | 0.32
-4 | 0.336
-3 | 0.352
-2 | 0.368
-1 | 0.384
0 | 0.4
1 | 0.42
2 | 0.44
3 | 0.46
4 | 0.48
5 | 0.5
6 | 0.526
7 | 0.552
8 | 0.578
9 | 0.604
10 | 0.63
11 | 0.666
12 | 0.702
13 | 0.738
14 | 0.774
15 | 0.81
16 | 0.848
17 | 0.886
18 | 0.924
19 | 0.962
20 | 1
21 | 1.05
22 | 1.1
23 | 1.15
24 | 1.2
25 | 1.25
26 | 1.316
27 | 1.382
28 | 1.448
29 | 1.514
30 | 1.58
31 | 1.664
32 | 1.748
33 | 1.832
34 | 1.872
35 | 2
36 | 2.1
37 | 2.2
38 | 2.3
39 | 2.4
40 | 2.5
41 | 2.628
42 | 2.756
43 | 2.884
44 | 3.012
45 | 3.15
46 | 3.316
47 | 3.482
48 | 3.648
49 | 3.814
50 | 3.98
51 | 4.184
52 | 4.388
53 | 4.592
54 | 4.796
55 | 5
56 | 5.26
57 | 5.52
58 | 5.78
59 | 6.04
60 | 6.3
61 | 6.62
62 | 6.94
63 | 7.26
64 | 7.58
65 | 7.9
66 | 8.32
67 | 8.74
68 | 9.16
69 | 9.58
70 | 10
71 | 10.52
72 | 11.04
73 | 11.56
74 | 12.08
75 | 12.6
76 | 13.24
77 | 13.88
78 | 14.52
79 | 15.16
80 | 15.8
81 | 16.64
82 | 17.48
83 | 18.32
84 | 19.16
85 | 20
86 | 21.04
87 | 22.08
88 | 23.12
89 | 24.16
90 | 25.2
91 | 26.45
92 | 27.7
93 | 28.95
94 | 30.2
95 | 31.6
96 | 33.28
97 | 34.96
98 | 36.64
99 | 38.32
100 | 40
101 | 42.08
102 | 44.16
103 | 46.24
104 | 48.32
105 | 50.4
106 | 52.96
107 | 55.52
108 | 58.08
109 | 60.64
110 | 63.2

## Temp Conv
Temperature Conversion
°F | °C
-11.2 | -24
-9.4 | -23
-7.6 | -22
-5.8 | -21
-4 | -20
-2.2 | -19
-0.4 | -18
1.4 | -17
3.2 | -16
5 | -15
6.8 | -14
8.6 | -13
10.4 | -12
12.2 | -11
14 | -10
15.8 | -9
17.6 | -8
19.4 | -7
21.2 | -6
23 | -5
24.8 | -4
26.6 | -3
28.4 | -2
30.2 | -1
32 | 0
33.8 | 1
35.6 | 2
37.4 | 3
39.2 | 4
41 | 5
42.8 | 6
44.6 | 7
46.4 | 8
48.2 | 9
50 | 10
51.8 | 11
53.6 | 12
55.4 | 13
57.2 | 14
59 | 15
60.8 | 16
62.6 | 17
64.4 | 18
66.2 | 19
68 | 20
69.8 | 21
71.6 | 22
73.4 | 23
75.2 | 24
77 | 25
78.8 | 26
80.6 | 27
82.4 | 28
84.2 | 29
86 | 30
87.8 | 31
89.6 | 32
91.4 | 33
93.2 | 34
95 | 35
96.8 | 36
98.6 | 37
100.4 | 38
102.2 | 39
104 | 40
105.8 | 41
107.6 | 42
109.4 | 43
111.2 | 44
113 | 45
114.8 | 46
116.6 | 47
118.4 | 48
120.2 | 49
122 | 50
123.8 | 51
125.6 | 52
127.4 | 53
129.2 | 54
131 | 55
132.8 | 56
134.6 | 57
136.4 | 58
138.2 | 59
140 | 60
141.8 | 61
143.6 | 62
145.4 | 63
147.2 | 64
149 | 65
150.8 | 66
152.6 | 67
154.4 | 68
156.2 | 69
158 | 70
159.8 | 71
161.6 | 72
163.4 | 73
165.2 | 74
167 | 75
168.8 | 76
170.6 | 77
172.4 | 78
174.2 | 79
176 | 80
177.8 | 81
179.6 | 82
181.4 | 83
183.2 | 84
185 | 85
186.8 | 86
188.6 | 87
190.4 | 88
192.2 | 89
194 | 90
195.8 | 91
197.6 | 92
199.4 | 93
201.2 | 94
203 | 95
204.8 | 96
206.6 | 97
208.4 | 98
210.2 | 99
212 | 100
213.8 | 101
215.6 | 102
217.4 | 103
219.2 | 104
221 | 105
222.8 | 106
224.6 | 107
226.4 | 108
228.2 | 109
230 | 110

## Dropdowns
Visual & Mechanical Inspectiom Dropdown Options |  | Long Time Settings
Select One |  | 1
Satisfactory |  | 0.99
Unsatisfactory |  | 0.98
Cleaned |  | 0.97
See Comments |  | 0.96
Not Applicable |  | 0.95
0.94
Insulation Resistance Unit Answer Choices |  | 0.93
kΩ | Kilo-Ohms | 0.92
MΩ | Mega-Ohms | 0.91
GΩ | Giga-Ohms | 0.9
0.89
Insulation Resistance Test Voltages |  | 0.88
250V |  | 0.87
500V |  | 0.86
1000V |  | 0.85
2500V |  | 0.84
5000V |  | 0.83
0.82
Contact Resistance |  | 0.81
μΩ | Micro-Ohms | 0.8
mΩ | Milli-Ohms | 0.79
Ω | Ohms | 0.78
0.77
Dielectric Withstand Unit Answer Choices |  | 0.76
μA | Mirco Amp | 0.75
mA | Milli Amp | 0.74
0.73
VLF Withstand Test Voltages |  | 0.72
Cable Rating | Test voltage | 0.71
5 | 10 | 0.7
8 | 13 | 0.69
15 | 21 | 0.68
20 | 26 | 0.67
25 | 32 | 0.66
28 | 36 | 0.65
30 | 38 | 0.64
35 | 44 | 0.63
46 | 57 | 0.62
69 | 84 | 0.61
0.6
0.59
0.58
Equipment Evaluation Result |  | 0.57
PASS |  | 0.56
FAIL |  | 0.55
LIMITED SERVICE |  | 0.54
0.53
Electronic Trip Breaker Trip Unit Dropdown |  | 0.52
LI |  | 0.51
LS |  | 0.5
LSI |  | 0.49
LSIG |  | 0.48
0.47
0.46
0.45
0.44
0.43
0.42
0.41
0.4